## Slide 1: RE Procurements in a High Penetration Grid Hawaii Case Study
Leon R. Roose, Esq.
Principal & Chief Technologist, GridSTART
International Workshop sponsored by the U.S. Agency for International Development (USAID)
Asia EDGE Competitive Procurement Dialogue
November 18-20, 2019
Conrad Bangkok
Bangkok, Thailand
Grid System Technologies Advanced Research Team
Hawaii Natural Energy Institute
School of Ocean & Earth Science & Technology
University of Hawaii at Manoa
1680 East-West Road, POST 109
Honolulu, Hawaii 96822
Marc M. Matsuura, PE
Sr. Smart Grid Program Manager, GridSTART

## Slide 2: How we got here and procurement path ahead
Hawaii RPS Goals
2015 - 15%
2020 - 30%
2030 - 40%
2040 - 70%
2045 - 100%
Loss of
Geothermal May 2018
Production
Source: Hawaiian Electric and Kaua’i Island Utiltiy Cooperative 2018 RPS Reports

## Slide 3: Procurement Methods have Evolved
Chart: Cumulative Installed PV, MW
| 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
 | 1.8 | 2.4 | 4.7 | 12 | 24 | 40 | 79 | 171 | 301 | 389 | 487 | 586 | 695 | 745
Competitive Bidding Framework
PURPA
Unsolicited proposals & Bilateral negotiations
for
As-Available RE Energy
Competitive Bidding
for
As-Available
RE Energy
Competitive Bidding
Take or Pay for Energy
Lump Sum Payments
Dispatchable

## Slide 4: Competative Bidding Framework
Required method of generation resource procurement in Hawaii
  Consistent with Integrated Resource Plan (Power Development Plan)
  Waivers may be allowed under certain circumstances if approved by the regulator (Hawaii Public Utilities Commission)
  Separate bid evaluation and self-build teams
  A Code of Conduct shall be signed by each utility employee involved in advancing a self-bid project or implementing the competitive bidding process
  No unauthorized oral or written contacts between employees on separate teams
  All bidders, including the self-bid team, to be treated the same in terms of access to information, time of receipt of information, and response to questions
A Commission approved Independent Observer is required when the utility intends to submit a self-bid project

## Slide 5: As-Available vs. Take or Pay vs. Lump sum
Utility only pays for energy export
Accounting is simple.
RE project bears the risk of curtailment and risk is priced into their energy price.
PPA curtailment order is reverse-chronological seniority.
Curtailment risk estimated with grid modeling and projection of utility operating practices and system changes over PPA term.
Utility bears a significant and increasing risk of litigation over curtailment events and practices.
As-Available
Take or Pay
Utility pays for available energy.
Available energy must be calculated during curtailment events or an average energy amount can be agreed to up front.
Risk is better placed; utility in best position to make grid and operational changes to reduce curtailment risk.
Utility bears the risk of curtailment which reduces the energy price; more bankable.
Litigation risk greatly reduced.
Lump Sum
Most recent structure used to procure “dispatchable” RE.
Unlocks more flexibility and grid benefits from resources.
Decouples payments from the energy production.
Sets target for project operational “availability” & MWh “performance”.
Further reduces developer risk / price.

## Slide 6: As-Available Curtailment Provisions
Curtailment is only allowed:
  to accommodate construction or maintenance of the grid
  when safety or reliability are in jeopardy
    to avoid excess energy events during light load conditions
    if the project fails to meet it performance requirements or does not operate in accordance with good engineering and operating practices
Curtailment is implemented in reverse chronological order according to each project’s non-appealable PUC approval order date; difficult to administer
Capacity of the project’s curtailment priority is adjusted downward if its Annual Contract Energy over four consecutive years is less than 60% of its initial Annual Contract Energy.

## Slide 7: Dispatchable RE Provisions
Grid Operator (utility) has full dispatch control of the facility’s output
Lump sum monthly payment ($/month) for fixed costs (capital)
Net energy payment ($/MWh) for variable costs, if any
Interconnection Cost Savings Rate ($/100,000 cost savings) for shared interconnection facilities
Liquidated damages assessed for not meeting availability requirements
Project defaults if availability factor is below 84% for more than 3 consecutive years
Liquidated damages assessed for not meeting a measured performance ratio of 95% (adjusted for degradation)
Project defaults if performance ratio is below “Tier 2” performance for more than 3 consecutive years

## Slide 8: Interconnection and Transmission Upgrades
Interconnection Requirements Study (IRS) Process
  System, planning and design information is provided in the RFP to enable bidders to effectively estimate cost for interconnection facilities.
  Cost of interconnection facilities and upgrades are also determined by utility for each bid and factored into its evaluation and development of a short list.
  Full IRS conducted for short list bids and provided to each bidder at the bidders expense.
  Bidders incorporate the IRS results into their bids and may be able to adjust their price. However, an increase in price triggers a re-evaluation of the short list.

## Slide 9: Interconnection and Transmission Upgrades (cont.)
Interconnection and system upgrade costs
  Bidder is responsible for the cost of interconnection facilities.
  Cost of “interconnection facilities” and “system upgrades” are determined for each bid and factored into the evaluation and development of a short list.
  Facilities from the Point of Interconnection to the Grid Connection Point will be owned by the Utility.
  Utility installs and maintains the system upgrades at its cost (this cost is considered in the bid evaluations).
  System Benefits and/or Betterments are also considered in the bid evaluations.

## Slide 10: Unit Cost Estimates

## Slide 11: Evolution of Performance Requirements
Chart: Cumulative Installed PV, MW
| 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
 | 1.8 | 2.4 | 4.7 | 12 | 24 | 40 | 79 | 171 | 301 | 389 | 487 | 586 | 695 | 745
Frequency and voltage ride-through
Voltage regulation
Ramp rate limits
Transient OV mitigation
Fully Dispatchable
Fault ride-through
Frequency regulation
Fast frequency response

## Slide 12: Other Technical Provisions
Day ahead production forecast
Project and meteorological data to support utility forecasting
Detailed equipment specific models
  Model escrow process

## Slide 13: Takeaways
Risk allocation and pricing mechanisms have evolved as lessons were learned, experience/confidence gained and system needs changed
  Continuous improvement; what works today may not be best for tomorrow
Characteristics of a successful competitive procurement:
  Requirements based on planning studies – understand needs & minimize surprises
  Provide as much information as possible - minimize unknowns
  Effective risk allocation and mitigation
  Clear requirements, process and schedule
There is no “free lunch.” Added Risks = Added cost
  Risk placed on the entity in best positioned and enabled to manage that risk
  Utility and RE projects require cost recovery for interconnection facilities and upgrades
    Who pays for infrastructure improvements depends on who can best manage cost and who benefits from the upgrades

## Slide 14
For more information, contact:
Marc M. Matsuura
Sr. Smart Grid Program Manager
GridSTART
Hawaii Natural Energy Institute
School of Ocean & Earth Science & Technology
University of Hawaii at Manoa
1680 East-West Road, POST 109
Honolulu, Hawaii 96822
Office: (808) 956-5070
Mobile: (808) 321-8928
E-mail: marc.matsuura@hawaii.edu
Website: www.hnei.hawaii.edu
Grid System Technologies Advanced Research Team
Mahalo! (Thank you)

## Slide 15
Grid System Technologies Advanced Research Team
Leon R. Roose
Chief Technologist
Mr. Roose is a tenured faculty member of the Hawaii Natural Energy Institute (HNEI), University of Hawaii, where he formed and leads GridSTART, (Grid System Technologies Advanced Research Team), a research team focused on the integration and analysis of energy technologies and power systems, including smart grid and micro grid applications.
He served in numerous leadership roles at the Hawaiian Electric Company for 19 years prior including management of renewable energy planning and integration, generation resource planning and competitive procurement, negotiation of all power purchase agreements for the utility, transmission and distribution system planning, smart grid planning and projects, system relaying and protection, and fuel purchase and supply to utility generating plants. He is a licensed attorney, worked in private law practice in Hawaii and was formerly Associate General Counsel at Hawaiian Electric. He holds a B.S. in Electrical Engineering and a J.D. from the University of Hawaii.

## Slide 16
Grid System Technologies Advanced Research Team
Marc M. Matsuura
Sr. Smart Grid Program Manager
Marc joined the Hawaii Natural Energy Institute (HNEI), School of Ocean & Earth Science & Technology, University of Hawaii at Manoa, in 2013 as the Senior Smart Grid Program Manager and is a founding member of GridSTART (Grid System Technologies Advanced Research Team).
Prior to joining HNEI, he was with the Hawaiian Electric Company for 21 years. His career at Hawaiian Electric included positions in the areas of Transmission & Distribution (T&D) Engineering, T&D Standards and Technical Services, System Operations, Transmission Planning, Smart Grid Planning, and System Integration. Marc is a licensed professional electrical engineer in Hawaii. He holds a B.S. in Electrical Engineering and an M.B.A. from the University of Hawaii.

## Slide 17: Hawaii Natural Energy Institute (HNEI) University of Hawai‘i at Mānoa
Organized Research Unit in School of Ocean and Earth Science and Technology (SOEST) Founded in 1974, established in Hawai‘i statute in 2007 (HRS 304A-1891)
Conduct RDT&E to accelerate and facilitate the use of resilient alternative energy technologies and reduce Hawaii’s dependence on fossil fuels.
Diverse staff includes engineers, scientists, lawyers; students and postdoctoral fellows; visiting scholars
Areas of Interest
  Policy and Innovation
  Grid Integration (GridSTART)
  Alternative Fuels
  Electrochemical Power Systems
  Renewable Power Generation
  Building Efficiency
  Transportation
Core Functions
State Energy Policy Support
Research & Development
Testing and Evaluation
Analysis
Workforce Development

## Slide 18
Serves to integrate into the operating power grid other HNEI technology areas: energy efficiency, renewable power generation, biomass and biofuels, fuel cells and hydrogen
Strong and growing partnerships with Hawaii, national and international organizations including Asia-Pacific nations
Established to develop and test advanced grid architectures, new technologies and methods for effective integration of renewable energy resources, power system optimization and resilience, and enabling policies
Lead for many public-private demonstration projects
Expertise & Focus:
Energy Policy
Renewable Energy Grid Integration
Smart Grid Planning & Technologies
Power Systems Planning
Power Systems Operation
Power Systems Engineering and Standards
Communications Design and Testing
Project Management and Execution

## Slide 19
Sampling of Sponsors & Partners:
* Prior electric utility company senior management and staff
* Prior Commissioner of the Hawaii State Public Utilities Commission
* Prior Administrator of the Hawaii State Energy Office
Core Team Members:
Richard Rocheleau Director, HNEI
Leon Roose * Specialist & Chief Technologist
Mark Glick * Specialist, Energy Policy
John Cole * Senior Policy Strategist
James Maskrey * Energy Efficiency Program Manager
Marc Matsuura * Senior Smart Grid Program Manager
Kanoa Jou * Power Systems Engineer
Staci Sadoyama * Power Systems Engineer
Thai Tran Junior Power System Engineer
Silas Oliviera de Toledo Junior Power System Engineer
Brian Chee Communications & IT System Analyst
Dax Mathews Renewable Energy Resources Forecasting
Kevin Davies Assistant Researcher
Saeed Sepasi Assistant Researcher
Jonathan Kobayashi Research Associate
Sharon Chan GIS Specialist
Yan Chen Post-Doctoral Fellow
Quynh Tran Post-Doctoral Fellow
Arif Rahman Post-Doctoral Fellow
Team members combine for 75+ years of utility and regulatory experience